# PROJECT STATUS REPORT / FIELD OBSERVATION

Project: MOSP Food Cart

Project Location: Mount Sinai Medical Center, 4300 Alton Road, Miami Beach, FL

Time: 09:00 AM (tentative)

Site Visit Date: 02/25/26

Weather: Clear / dry conditions

Phase: Construction Administration

Status: Work in progress. Temporary containment and negative pressure controls observed in active area.

Present: Eduardo Muhiña (RDG)

NOTE: Omission of any item of non-compliance from this report does not relieve the contractor of responsibility to comply with contract documents and applicable code requirements.

## MOSP Food Cart

| ITEM # | DESCRIPTION | REFERENCE PHOTO/DETAIL | COMPLETED YES or NO |
| --- | --- | --- | --- |
| 1 | Exterior temporary containment and protection barriers are in place around active work area. Maintain sealed perimeter and controlled access at all times. | Photo 1, 2, 3, 4 | YES |
| 2 | Work zone remains demarcated with warning tape and temporary framing/plastic barriers. Continue maintaining separation from adjacent occupied areas. | Photo 1, 3, 7 | YES |
| 3 | Negative pressure monitoring device (Magnehelic) observed installed and operating. Continue continuous monitoring per ICRA/infection control protocol. | Photo 5 | YES |
| 4 | Negative air pressure log present on site. Ensure readings are logged per required intervals and signed by responsible party. | Photo 6 | YES |
| 5 | Barrier condition appears generally adequate; verify all joints/penetrations remain sealed to prevent air leakage. | Photo 3, 4, 7 | NO (verify and maintain) |
| 6 | Housekeeping in perimeter work area should remain ongoing to reduce dust/debris migration. Maintain daily cleanup and disposal routine. | Photo 2, 4 | NO (ongoing item) |
| 7 | Continue documenting pressure compliance and barrier integrity until area turnover/inspection. | Photo 5, 6, 7 | NO (ongoing item) |
| 8 | Project identification and location confirmed against reference documentation. | Photo 8 | YES |

## Recommended Next Steps

1. Maintain and document negative pressure continuously.

2. Re-check all barrier seals/penetrations at each shift.

3. Continue daily housekeeping and dust control.

4. Keep updated field log for CA record and closeout support.